## Modbus
Register Address (DEC) | Register Address (HEX) | Meaning | Registers | Read/ Write | Decimals | Notes
12 | 0x000C | Baud rate and slave address | 1 | RW | 1 | High bytes are baud rates, low bytes are communication addresses. If 02 03 02 02 03 BD 25 is read out, it means that the baud rate status word is 0x02 and the communication address is 0x03
14 | 0x000E | Phase A voltage | 1 | R | 100 | 220.00V
15 | 0x000F | Phase B voltage | 1 | R | 100
16 | 0x0010 | Phase C voltage | 1 | R | 100
17 | 0x0011 | Phase A current | 2 | R | 1000 | 5.000A All double character data is high word first, low word next register
19 | 0x0013 | Phase B current | 2 | R | 1000
21 | 0x0015 | Phase C current | 2 | R | 1000
23 | 0x0017 | Total active power | 2 | R | 10 | Total power across 3 phases, 1 decimal places
25 | 0x0019 | Phase A active power | 2 | R | 10
27 | 0x001B | Phase B active power | 2 | R | 10
29 | 0x001D | Phase C active power | 2 | R | 10
31 | 0x001F | Total reactive power | 2 | R | 10 | var
33 | 0x0021 | Phase A reactive power | 2 | R | 10
35 | 0x0023 | Phase B reactive power | 2 | R | 10
37 | 0x0025 | Phase C reactive power | 2 | R | 10
39 | 0x0027 | Total apparent power | 2 | R | 10 | VA
41 | 0x0029 | Phase A apparent power | 2 | R | 10
43 | 0x002B | Phase B apparent power | 2 | R | 10
45 | 0x002D | Phase C apparent power | 2 | R | 10
47 | 0x002F | Total power factor | 1 | R | 1000
48 | 0x0030 | Phase A power factor | 1 | R | 1000
49 | 0x0031 | Phase B power factor | 1 | R | 1000
50 | 0x0032 | Phase C power factor | 1 | R | 1000
51 | 0x0033 | Frequency | 1 | R | 100 | 50.00Hz
52 | 0x0034 | Total power | 2 | R | 100 | 1.00kWh
54 | 0x0036 | Phase A electricity | 2 | R | 100
56 | 0x0038 | Phase B electricity | 2 | R | 100
58 | 0x003A | Phase C electricity | 2 | R | 100
60 | 0x003C | Temperature | 1 | R | 1 | 25℃
61 | 0x003D | Runtime | 1 | R |  | minutes
62 | 0x003E | Alarm marker | 1 | R |  | bit marker: 0: Overvoltage 1: Undervoltage 2: Overcurrent 3: Overpower 4: Over-current 5: Over-temperature 6: Voltage imbalance 7: Current balance
63 | 0x003F | Meter status | 1 | RW |  | 0: Output off 1: Output on Only single words are allowed to be written
64 | 0x0040 | Overvoltage | 1 | RW | 10 | 240.0V max=290.0 允许以下一起读写
65 | 0x0041 | Undervoltage | 1 | RW | 10 | 120.0V max=220.0
66 | 0x0042 | Overcurrent | 1 | RW | 100 | 20.00A max=99.00
67 | 0x0043 | Overpower | 1 | RW | 100 | 1.00kW max=23.20
68 | 0x0044 | Voltage imbalance | 1 | RW | 10 | 10.0V max=290.0
69 | 0x0045 | Current imbalance | 1 | RW | 10 | 1.0A max=99.0
70 | 0x0046 | countdown | 1 | RW | 1 | minutes max=59999
71 | 0x0047 | Screensaver | 1 | RW | 1 | minutes max=59
72 | 0x0048 | Over temperature | 1 | RW | 1 | ℃ max=150
73 | 0x0049 | Over electricity | 2 | RW | 1 | kWh max=9999999
75 | 0x004b | Clear electricity usage | 1 | W | 1 | 0x5aa5 Zero only allows single-word writing
76 | 0x004c | Meter cleared | 1 | W | 1 | 0x5aa5 Zero only allows single-word writing